## HIOReportOutput
Region | NSP | Start | Finish | Network Asset | Impact | Recall | Status | Status and Market Notice | Project Work? | Unplanned? | DNSP Aware? | Generator Aware? | Inter-Regional | Impact Region, Reason and Duration | Vs Old | Duration
NSW | Transgrid | 2024-05-21 07:00 | 2024-05-25 17:00 | Liddell to Muswellbrook (83) 330 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 4 hrs-Night: 4 hrs | Withdrawn | Withdrawn | [5 empty] | NSW / QLD Commissioning 4.4 Days | #VALUE! | 4.4 Days
QLD | Powerlink | 2024-05-22 07:00 | 2024-05-23 16:00 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T |  | QLD Commissioning 1.4 Days | #VALUE! | 1.4 Days
TAS | TasNetworks | 2024-05-28 08:00 | 2024-05-31 14:00 | Sheffield - Farrell No.2 220 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 24 hrs-Night: 24 hrs | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  | T |  | TAS Commissioning 3.3 Days | #VALUE! | 3.3 Days
TAS | TasNetworks | 2024-06-01 08:00 | 2024-06-01 14:30 | Sheffield - Farrell No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  |  | T |  | Commissioning 6.5 Hours | #VALUE! | 6.5 Hours
NSW | Transgrid | 2024-06-03 07:00 | 2024-06-03 18:00 | Tamworth No.3 330 kV Bus | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 8 hrs-Night: 8 hrs | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Commissioning 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-06-04 06:00 | 2024-06-04 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-04 06:00 | 2024-06-04 18:00 | Heywood - Mortlake 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-05 06:00 | 2024-06-05 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-05 07:00 | 2024-06-05 16:00 | Hazelwood - Rowville 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9 Hours | #VALUE! | 9 Hours
QLD | Powerlink | 2024-06-05 10:00 | 2024-06-07 16:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 2 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 2.3 Days | #VALUE! | 2.3 Days
VIC | AusNet | 2024-06-06 06:00 | 2024-06-06 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
SA | ElectraNet | 2024-06-06 07:30 | 2024-06-09 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | SA Maintenance 3.4 Days | #VALUE! | 3.4 Days
TAS | TasNetworks | 2024-06-06 10:30 | 2024-06-06 15:00 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  |  | T |  | Maintenance 4.5 Hours | #VALUE! | 4.5 Hours
VIC | AusNet | 2024-06-07 06:00 | 2024-06-07 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-08 06:00 | 2024-06-08 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-09 06:00 | 2024-06-09 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-10 06:00 | 2024-06-10 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-10 07:00 | 2024-06-10 17:00 | Moorabool–Sydenham No.2 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 1 hr-Night: NA | Withdrawn | Withdrawn | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-06-11 06:00 | 2024-06-11 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
NSW | Transgrid | 2024-06-11 07:00 | 2024-06-13 18:00 | Tamworth No.3 330 kV Bus | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 8 hrs-Night: 8 hrs | Planned - MTLTP | Planned - MTLTP | [5 empty] | NSW / QLD Commissioning 2.5 Days | #VALUE! | 2.5 Days
SA | ElectraNet | 2024-06-11 07:30 | 2024-06-17 07:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - MTLTP | Planned - MTLTP |  |  |  |  | T | SA Maintenance 6 Days | #VALUE! | 6 Days
VIC | AusNet | 2024-06-12 06:00 | 2024-06-12 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-12 07:00 | 2024-06-12 18:00 | Jindera - Wodonga (060) 330 kV Line | <<This outage has been WITHDRAWN!>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | NSW/ VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-06-13 06:00 | 2024-06-13 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-13 07:00 | 2024-06-13 17:00 | Jindera - Wodonga (060) 330 kV Line | <<This outage has been WITHDRAWN!>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | NSW/ VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-06-14 06:00 | 2024-06-14 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-14 07:00 | 2024-06-14 17:00 | Jindera - Wodonga (060) 330 kV Line | <<This outage has been WITHDRAWN!>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | NSW/ VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-06-15 06:00 | 2024-06-15 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-15 06:00 | 2024-06-15 18:00 | Jindera - Wodonga (060) 330 kV Line | <<This outage has been WITHDRAWN!>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | NSW/ VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-16 06:00 | 2024-06-16 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-16 06:00 | 2024-06-16 18:00 | Jindera - Wodonga (060) 330 kV Line | <<This outage has been WITHDRAWN!>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | NSW/ VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-17 06:00 | 2024-06-17 18:00 | Moorabool - Mortlake 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-18 06:00 | 2024-06-18 18:00 | Moorabool - Mortlake 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-18 07:00 | 2024-06-18 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
SA | ElectraNet | 2024-06-18 07:30 | 2024-06-24 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2024-06-18 09:00 | 2024-06-20 16:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 2.3 Days | #VALUE! | 2.3 Days
VIC | AusNet | 2024-06-19 06:00 | 2024-06-19 18:00 | Moorabool - Mortlake 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-06-19 07:30 | 2024-06-19 16:30 | Jindera - Wodonga (060) 330 kV Line | <<NEW since the last notification>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 9 Hours | #VALUE! | 9 Hours
VIC | AusNet | 2024-06-20 07:30 | 2024-06-20 16:30 | Jindera - Wodonga (060) 330 kV Line | <<NEW since the last notification>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 9 Hours | #VALUE! | 9 Hours
SA | ElectraNet | 2024-06-20 16:30 | 2024-06-22 16:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 2 Days | #VALUE! | 2 Days
VIC | AusNet | 2024-06-21 07:30 | 2024-06-21 16:30 | Jindera - Wodonga (060) 330 kV Line | <<NEW since the last notification>> This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 9 Hours | #VALUE! | 9 Hours
VIC | AusNet | 2024-06-25 07:00 | 2024-06-25 18:00 | Jindera - Wodonga (060) 330 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 11 Hours | #VALUE! | 11 Hours
QLD | Powerlink | 2024-06-25 08:00 | 2024-06-27 16:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 2 hrs-Night: 6 hrs | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | QLD Commissioning 2.3 Days | #VALUE! | 2.3 Days
VIC | AusNet | 2024-06-26 07:00 | 2024-06-26 17:00 | Jindera - Wodonga (060) 330 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-06-27 07:00 | 2024-06-27 17:00 | Jindera - Wodonga (060) 330 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Maintenance 10 Hours | #VALUE! | 10 Hours
SA | ElectraNet | 2024-06-29 08:30 | 2024-06-29 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 9 Hours | #VALUE! | 9 Hours
SA | ElectraNet | 2024-06-30 07:30 | 2024-07-05 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | SA Maintenance 5.4 Days | #VALUE! | 5.4 Days
VIC | AusNet | 2024-07-01 06:00 | 2024-07-01 21:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 15 Hours | #VALUE! | 15 Hours
VIC | AusNet | 2024-07-02 06:00 | 2024-07-02 18:00 | Moorabool - Haunted Gully 500 kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-02 06:00 | 2024-07-02 18:00 | Moorabool - Haunted Gully 500 kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-03 07:00 | 2024-07-03 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-07-05 06:00 | 2024-07-05 21:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 15 Hours | #VALUE! | 15 Hours
VIC | AusNet | 2024-07-05 07:00 | 2024-07-05 16:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9 Hours | #VALUE! | 9 Hours
SA | ElectraNet | 2024-07-06 07:30 | 2024-07-07 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 1.5 Days | #VALUE! | 1.5 Days
SA | ElectraNet | 2024-07-08 07:30 | 2024-07-10 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 2.4 Days | #VALUE! | 2.4 Days
VIC | TOA | 2024-07-09 06:00 | 2024-07-09 18:00 | Ararat - Crowlands 220kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  | T | T | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-09 07:00 | 2024-07-09 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-07-10 06:00 | 2024-07-10 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-10 06:00 | 2024-07-10 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | TOA | 2024-07-10 06:00 | 2024-07-10 18:00 | Ararat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T | T | Commissioning 12 Hours | #VALUE! | 12 Hours
QLD | Powerlink | 2024-07-10 09:00 | 2024-07-10 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 8 Hours | #VALUE! | 8 Hours
QLD | Powerlink | 2024-07-11 07:00 | 2024-07-11 15:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 8 Hours | #VALUE! | 8 Hours
VIC | AusNet | 2024-07-18 06:00 | 2024-07-18 18:00 | Moorabool - Haunted Gully 500 kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-19 06:00 | 2024-07-19 18:00 | Moorabool - Haunted Gully 500 kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
SA | ElectraNet | 2024-07-25 07:30 | 2024-08-03 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | SA Maintenance 9.4 Days | #VALUE! | 9.4 Days
SA | ElectraNet | 2024-07-26 07:45 | 2024-07-27 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 5 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 1.4 Days | #VALUE! | 1.4 Days
VIC | AusNet | 2024-07-29 06:00 | 2024-07-29 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-07-30 06:00 | 2024-07-30 18:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
SA | ElectraNet | 2024-07-31 07:45 | 2024-08-01 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 5 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 1.4 Days | #VALUE! | 1.4 Days
VIC | AusNet | 2024-08-03 06:00 | 2024-08-03 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Commissioning 12 Hours | #VALUE! | 12 Hours
SA | ElectraNet | 2024-08-03 07:45 | 2024-08-04 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 5 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 1.4 Days | #VALUE! | 1.4 Days
VIC | AusNet | 2024-08-05 06:00 | 2024-08-05 18:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-05 06:00 | 2024-08-07 18:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 2.5 Days | #VALUE! | 2.5 Days
SA | ElectraNet | 2024-08-05 07:30 | 2024-08-11 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
VIC | AusNet | 2024-08-06 06:00 | 2024-08-06 18:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
QLD | Powerlink | 2024-08-06 12:05 | 2024-08-06 15:00 | Haughton River No. 2 275kV BUS | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | QLD Maintenance 2.9 Hours | #VALUE! | 2.9 Hours
VIC | AusNet | 2024-08-07 06:00 | 2024-08-07 18:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-19 07:00 | 2024-08-19 17:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-19 07:00 | 2024-08-19 17:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-20 06:00 | 2024-08-20 18:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-21 07:00 | 2024-08-21 17:00 | Horsham - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-21 07:00 | 2024-08-21 17:00 | Horsham - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-22 07:00 | 2024-08-22 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-08-23 07:00 | 2024-08-23 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-08-24 07:00 | 2024-08-24 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-25 06:00 | 2024-08-25 18:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-25 07:00 | 2024-08-25 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-26 07:00 | 2024-08-26 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-26 07:00 | 2024-08-26 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-27 07:00 | 2024-08-27 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-27 07:00 | 2024-08-27 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
QLD | Powerlink | 2024-08-27 08:00 | 2024-08-31 16:00 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.3 Days | #VALUE! | 4.3 Days
VIC | AusNet | 2024-08-28 07:00 | 2024-08-28 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-28 07:00 | 2024-08-28 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-29 07:00 | 2024-08-29 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-29 07:00 | 2024-08-29 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-08-30 07:00 | 2024-08-30 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-08-31 07:00 | 2024-08-31 18:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-08-31 07:00 | 2024-08-31 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-01 07:00 | 2024-09-01 18:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2024-09-01 07:00 | 2024-09-01 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-02 07:00 | 2024-09-02 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-02 07:00 | 2024-09-02 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-03 07:00 | 2024-09-03 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-09-03 07:00 | 2024-09-03 19:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
QLD | Powerlink | 2024-09-05 07:30 | 2024-09-05 17:00 | Nebo - Strathmore (8845) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 9.5 Hours | #VALUE! | 9.5 Hours
NSW | Transgrid | 2024-09-09 05:30 | 2024-09-09 22:00 | Balranald - Darlington Point (X5) 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C During this planned outage power transfer will be restricted • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T | T | NSW / VIC Commissioning 16.5 Hours | #VALUE! | 16.5 Hours
VIC | AusNet | 2024-09-09 07:00 | 2024-09-09 17:00 | Hazelwood - South Morang No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-09 07:00 | 2024-09-09 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-10 07:00 | 2024-09-12 18:00 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 2.5 Days | #VALUE! | 2.5 Days
VIC | AusNet | 2024-09-10 07:00 | 2024-09-10 17:00 | Hazelwood - South Morang No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-11 07:30 | 2024-09-11 17:00 | Hazelwood - South Morang No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9.5 Hours | #VALUE! | 9.5 Hours
VIC | AusNet | 2024-09-12 07:30 | 2024-09-12 17:00 | Hazelwood - South Morang No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9.5 Hours | #VALUE! | 9.5 Hours
VIC | AusNet | 2024-09-16 07:00 | 2024-09-16 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
TAS | TasNetworks | 2024-09-17 14:00 | 2024-09-17 16:30 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT |  |  |  | T |  | TAS Maintenance 2.5 Hours | #VALUE! | 2.5 Hours
VIC | AusNet | 2024-09-23 07:00 | 2024-09-23 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-09-24 07:00 | 2024-09-26 18:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 24 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 2.5 Days | #VALUE! | 2.5 Days
NSW | Transgrid | 2024-09-30 05:30 | 2024-09-30 22:00 | Jindera - Wagga (62) 330 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Commissioning 16.5 Hours | #VALUE! | 16.5 Hours
VIC | AusNet | 2024-09-30 07:00 | 2024-09-30 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-07 06:00 | 2024-10-07 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-12 06:00 | 2024-10-12 16:00 | Ararat - Crowlands 220kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-14 06:00 | 2024-10-14 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-15 06:00 | 2024-10-20 17:00 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.5 Days | #VALUE! | 5.5 Days
VIC | AusNet | 2024-10-21 06:00 | 2024-10-21 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-25 06:00 | 2024-10-25 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-10-26 06:00 | 2024-10-26 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-10-27 06:00 | 2024-10-27 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
TAS | TasNetworks | 2024-10-28 05:00 | 2024-11-01 20:00 | George Town - George Town Converter Station 220 kV Line | Tasmania will be separated from the NEM | Day: 4 hrs-Night: 6 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Maintenance 4.6 Days | #VALUE! | 4.6 Days
VIC | AusNet | 2024-10-28 06:00 | 2024-10-28 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-10-28 06:00 | 2024-10-28 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-10-29 06:00 | 2024-10-29 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
TAS | TasNetworks | 2024-10-30 13:00 | 2024-10-30 15:30 | Gordon - Chapel St No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  | T |  | TAS Commissioning 2.5 Hours | #VALUE! | 2.5 Hours
VIC | AusNet | 2024-10-31 05:00 | 2024-10-31 17:00 | Kerang-Wemen 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2024-11-01 06:00 | 2024-11-01 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-04 06:00 | 2024-11-04 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-09 06:00 | 2024-11-09 16:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-11 06:00 | 2024-11-11 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-12 06:00 | 2024-11-12 16:00 | Ararat - Crowlands 220kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-18 06:00 | 2024-11-18 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-11-25 06:00 | 2024-11-25 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
QLD | Powerlink | 2024-11-25 08:00 | 2024-11-29 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T |  |  | QLD Maintenance 4.4 Days | #VALUE! | 4.4 Days
VIC | AusNet | 2024-12-02 06:00 | 2024-12-02 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-12-09 06:00 | 2024-12-09 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2024-12-09 06:00 | 2024-12-09 16:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
QLD | Powerlink | 2024-12-09 08:00 | 2024-12-11 17:00 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 6 hrs-Night: 8 hrs | Planned - RESUBMIT | Planned - RESUBMIT |  |  |  | T |  | QLD Commissioning 2.4 Days | #VALUE! | 2.4 Days
VIC | AusNet | 2024-12-31 06:00 | 2024-12-31 17:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #VALUE! | 11 Hours
VIC | AusNet | 2025-01-04 06:00 | 2025-01-04 16:00 | Bulgana - Horsham 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-01-04 06:00 | 2025-01-04 16:00 | Crowland - Bulgana 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-01-13 06:00 | 2025-01-13 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-01-14 06:00 | 2025-01-14 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-01-20 06:00 | 2025-01-20 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-01-27 06:00 | 2025-01-27 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-03 06:00 | 2025-02-03 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-03 06:00 | 2025-02-03 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-02-04 06:00 | 2025-02-04 16:00 | Bulgana - Horsham 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-04 06:00 | 2025-02-04 16:00 | Crowland - Bulgana 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-04 06:00 | 2025-02-04 16:00 | Bulgana - Horsham 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-10 06:00 | 2025-02-10 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-17 06:00 | 2025-02-17 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-02-21 06:00 | 2025-02-21 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-02-22 06:00 | 2025-02-22 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-02-23 06:00 | 2025-03-23 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 28.5 Days | #VALUE! | 28.5 Days
VIC | AusNet | 2025-02-24 06:00 | 2025-02-24 16:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-03-03 06:00 | 2025-03-03 16:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
QLD | Powerlink | 2025-03-03 08:00 | 2025-03-07 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 4.4 Days | #VALUE! | 4.4 Days
VIC | AusNet | 2025-03-04 06:00 | 2025-03-04 16:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-03-04 06:00 | 2025-03-04 16:00 | Horsham - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-03-07 05:00 | 2025-03-13 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 6.5 Days | #VALUE! | 6.5 Days
QLD | Powerlink | 2025-03-07 17:01 | 2025-08-19 07:59 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 164.6 Days | #VALUE! | 164.6 Days
VIC | AusNet | 2025-03-10 06:00 | 2025-03-10 16:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-03-17 06:00 | 2025-03-19 16:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 2.4 Days | #VALUE! | 2.4 Days
VIC | AusNet | 2025-03-28 06:00 | 2025-03-28 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #VALUE! | 12 Hours
VIC | AusNet | 2025-04-02 06:00 | 2025-04-02 16:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-02 06:00 | 2025-04-02 16:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Kiamal SF - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Horsham - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Horsham - MurraWarra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-04-05 06:00 | 2025-04-10 18:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.5 Days | #VALUE! | 5.5 Days
VIC | AusNet | 2025-04-06 12:00 | 2025-04-06 17:00 | Moorabool - Mortlake 500 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC / SA Maintenance 5 Hours | #VALUE! | 5 Hours
VIC | AusNet | 2025-04-10 07:00 | 2025-04-10 17:00 | Rowville - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
QLD | Powerlink | 2025-04-23 08:00 | 2025-05-09 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 16.4 Days | #VALUE! | 16.4 Days
VIC | AusNet | 2025-05-07 07:00 | 2025-05-07 17:00 | Dederang - Wodonga 330 kV Line | This is a high-impact outage if the forecast temperature at Red Cliffs is greater than 30 deg. C. This line outage offloads X5 220 kV line. Possible load shedding and risk of large reduction in generation in NSW and interconnector capacity between NSW - Victoria following a credible contingency | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-08 07:00 | 2025-05-08 17:00 | Dederang - Wodonga 330 kV Line | This is a high-impact outage if the forecast temperature at Red Cliffs is greater than 30 deg. C. This line outage offloads X5 220 kV line. Possible load shedding and risk of large reduction in generation in NSW and interconnector capacity between NSW - Victoria following a credible contingency | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-20 07:00 | 2025-05-20 17:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-21 07:00 | 2025-05-21 17:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-21 07:00 | 2025-05-21 17:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-21 07:00 | 2025-05-21 17:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #VALUE! | 10 Hours
VIC | AusNet | 2025-05-22 07:00 | 2025-05-22 15:00 | Ballarat - Waubra 220 kV Line | This is a high-impact outage only if the forecast temperature at Red Cliffs is greater than 30 °C A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 8 Hours | #VALUE! | 8 Hours
VIC | AusNet | 2025-06-24 07:00 | 2025-06-29 17:00 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #VALUE! | 5.4 Days
SA | ElectraNet | 2025-06-30 07:30 | 2025-07-06 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2025-07-07 07:30 | 2025-07-13 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2025-07-14 07:30 | 2025-07-20 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.5 Days | #VALUE! | 6.5 Days
VIC | AusNet | 2025-07-15 07:00 | 2025-07-20 17:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #VALUE! | 5.4 Days
SA | ElectraNet | 2025-07-21 07:30 | 2025-07-27 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2025-07-28 07:30 | 2025-08-03 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2025-08-04 07:30 | 2025-08-10 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
VIC | AusNet | 2025-08-08 07:00 | 2025-08-13 17:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #VALUE! | 5.4 Days
QLD | Powerlink | 2025-08-19 08:00 | 2025-11-24 07:59 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 97 Days | #VALUE! | 97 Days
VIC | AusNet | 2025-09-01 07:00 | 2025-09-06 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #VALUE! | 5.4 Days
QLD | Powerlink | 2025-09-02 08:00 | 2025-09-15 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 13.4 Days | #VALUE! | 13.4 Days
QLD | Powerlink | 2025-11-03 07:00 | 2025-11-07 15:00 | Nebo - Broadsound (8846) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 8 hrs-Night: 8 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.3 Days | #VALUE! | 4.3 Days
QLD | Powerlink | 2025-11-24 08:00 | 2025-11-28 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 4.4 Days | #VALUE! | 4.4 Days
QLD | Powerlink | 2025-12-25 08:00 | 2026-01-07 17:00 | Strathmore - Ross (8858) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 72 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 13.4 Days | #VALUE! | 13.4 Days
SA | ElectraNet | 2026-06-29 07:30 | 2026-07-05 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2026-07-06 07:30 | 2026-07-12 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2026-07-13 07:30 | 2026-07-19 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.5 Days | #VALUE! | 6.5 Days
SA | ElectraNet | 2026-07-20 07:30 | 2026-07-26 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2026-07-27 07:30 | 2026-08-02 17:30 | Tailem Bend (6536) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2026-08-03 07:30 | 2026-08-09 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2027-06-28 07:30 | 2027-07-04 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2027-07-05 07:30 | 2027-07-11 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2027-07-12 07:30 | 2027-07-18 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.5 Days | #VALUE! | 6.5 Days
SA | ElectraNet | 2027-07-19 07:30 | 2027-07-25 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2027-07-26 07:30 | 2027-08-01 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2027-08-02 07:30 | 2027-08-08 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2028-06-26 07:30 | 2028-07-02 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2028-07-03 07:30 | 2028-07-09 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2028-07-10 07:30 | 2028-07-16 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.5 Days | #VALUE! | 6.5 Days
SA | ElectraNet | 2028-07-17 07:30 | 2028-07-23 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2028-07-24 07:30 | 2028-07-30 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2028-07-31 07:30 | 2028-08-06 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2029-07-02 07:30 | 2029-07-08 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2029-07-09 07:30 | 2029-07-15 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2029-07-16 07:30 | 2029-07-22 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.5 Days | #VALUE! | 6.5 Days
SA | ElectraNet | 2029-07-23 07:30 | 2029-07-29 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2029-07-30 07:30 | 2029-08-05 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2029-08-06 07:30 | 2029-08-12 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2030-07-01 07:30 | 2030-07-07 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2030-07-08 07:30 | 2030-07-14 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2030-07-15 07:30 | 2030-07-21 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #VALUE! | 6.5 Days
SA | ElectraNet | 2030-07-22 07:30 | 2030-07-28 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2030-07-29 07:30 | 2030-08-04 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
SA | ElectraNet | 2030-08-05 07:30 | 2030-08-11 17:30 | Tailem Bend (6595) 275 kV Circuit Breaker | A credible contingency event during this planned outage could leave South Australia connected to the NEM only via the South Australian 132 kV network. To maintain system security following this contingency AEMO will need to: • Initiate the orderly separation of SA from the rest of the NEM. • Source increased local regulation FCAS within SA. During this planned outage power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | Maintenance 6.4 Days | #VALUE! | 6.4 Days
Withdrawn / UTP since the last notification