## HIOReportOutput
Region | NSP | Start | Finish | Network Asset | Impact | Recall | Status | Status and Market Notice | Project Work? | Unplanned? | DNSP Aware? | Generator Aware? | Inter-Regional | Impact Region, Reason and Duration | Vs Old | Duration
VIC | AusNet | 2025-02-25 06:00 | 2025-02-25 15:00 | Dederang - Wodonga 330 kV Line | This line outage offloads X5 220 kV line. Possible load shedding and risk of large reduction in generation in NSW and interconnector capacity between NSW - Victoria following a credible contingency | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | VIC Maintenance 9 Hours | #REF! | 9 Hours
TAS | TasNetworks | 2025-02-27 07:00 | 2025-02-27 15:00 | Sheffield - Farrell No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - STLTP | Planned - STLTP |  |  |  | T |  | TAS Commissioning 8 Hours | #REF! | 8 Hours
NSW | Transgrid | 2025-03-03 06:00 | 2025-03-03 15:00 | Tamworth Liddell PS (84) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Commissioning 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-03-04 06:00 | 2025-03-04 15:00 | Tamworth Liddell PS (84) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Commissioning 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-03-05 06:00 | 2025-03-05 15:00 | Tamworth Liddell PS (84) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Commissioning 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-03-11 06:30 | 2025-03-11 15:30 | Muswellbrook - Tamworth (88) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Maintenance 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-03-12 06:30 | 2025-03-12 15:30 | Muswellbrook - Tamworth (88) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2025-03-12 07:00 | 2025-03-12 07:30 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - MTLTP | Planned - MTLTP | [5 empty] | QLD Maintenance 30 Minutes | #REF! | 30 Minutes
QLD | Powerlink | 2025-03-12 07:31 | 2025-03-12 17:00 | Strathmore - Ross (8857) 275 kV Line | <<This outage has been WITHDRAWN!>> This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Withdrawn | Withdrawn |  |  | T |  |  | QLD Commissioning 9.5 Hours | #REF! | 9.5 Hours
VIC | AusNet | 2025-03-12 11:00 | 2025-03-12 16:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 1 hr-Night: NA | Planned - MTLTP | Planned - MTLTP | [5 empty] | VIC / SA Maintenance 5 Hours | #REF! | 5 Hours
VIC | AusNet | 2025-03-13 05:30 | 2025-03-13 15:00 | Hazelwood - Loy Yang Power Station No.3 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP | [5 empty] | VIC Maintenance 9.5 Hours | #REF! | 9.5 Hours
NSW | Transgrid | 2025-03-13 06:30 | 2025-03-13 15:30 | Muswellbrook - Tamworth (88) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Maintenance 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-03-14 06:30 | 2025-03-14 15:30 | Muswellbrook - Tamworth (88) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP |  |  | T | T | T | NSW / QLD Maintenance 9 Hours | #REF! | 9 Hours
QLD | Powerlink | 2025-03-15 14:30 | 2025-03-15 15:00 | Strathmore - Ross (8857) 275 kV Line | <<This outage has been WITHDRAWN!>> This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Withdrawn | Withdrawn | [5 empty] | QLD Maintenance 30 Minutes | #REF! | 30 Minutes
QLD | Powerlink | 2025-03-15 15:30 | 2025-03-15 16:00 | Strathmore - Ross (8857) 275 kV Line | <<NEW since the last notification>> This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | QLD Maintenance 30 Minutes | #REF! | 30 Minutes
QLD | Powerlink | 2025-03-17 08:00 | 2025-03-21 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: 48 hrs | Planned - MTLTP | Planned - MTLTP | [5 empty] | QLD Maintenance 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-03-18 05:00 | 2025-03-18 18:00 | Jindera - Wodonga (060) 330 kV Line | This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  | T |  | T | NSW / VIC Maintenance 13 Hours | #REF! | 13 Hours
VIC | AusNet | 2025-03-19 05:00 | 2025-03-19 18:00 | Jindera - Wodonga (060) 330 kV Line | This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  | T |  | T | NSW / VIC Maintenance 13 Hours | #REF! | 13 Hours
VIC | AusNet | 2025-03-19 06:00 | 2025-03-19 11:00 | Keilor - South Morang 500 kV Line | <<NEW since the last notification>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5 Hours | #REF! | 5 Hours
VIC | AusNet | 2025-03-20 05:00 | 2025-03-20 18:00 | Jindera - Wodonga (060) 330 kV Line | This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  | T |  | T | NSW / VIC Maintenance 13 Hours | #REF! | 13 Hours
QLD | Powerlink | 2025-03-21 17:01 | 2025-09-02 07:59 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - MTLTP | Planned - MTLTP | [5 empty] | QLD Maintenance 164.6 Days | #REF! | 164.6 Days
VIC | AusNet | 2025-03-22 05:00 | 2025-03-22 17:00 | Rowville - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-03-23 05:00 | 2025-03-23 17:00 | Rowville - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-03-27 06:00 | 2025-03-28 16:00 | Rowville - South Morang 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - MTLTP | Planned - MTLTP | [5 empty] | VIC Maintenance 1.4 Days | #REF! | 1.4 Days
VIC | AusNet | 2025-03-30 06:00 | 2025-03-30 16:00 | Moorabool–Sydenham No.2 500 kV Line | <<This outage has been WITHDRAWN!>> A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Withdraw Requested | Withdraw Requested | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
NSW | Transgrid | 2025-04-01 06:00 | 2025-04-01 16:00 | Kiamal SF - Red Cliffs 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T | T | NSW/VIC Commissioning 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-04-02 08:00 | 2025-04-02 17:00 | Nebo - Broadsound (8846) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 15 mins-Night: 15 mins | Planned - RESUBMIT | Planned - RESUBMIT |  |  | T | T |  | QLD Maintenance 9 Hours | #REF! | 9 Hours
NSW | Transgrid | 2025-04-03 06:00 | 2025-04-03 16:00 | Kiamal SF - Red Cliffs 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T | T | NSW/VIC Commissioning 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-04-03 08:00 | 2025-04-03 13:00 | Nebo - Broadsound (8846) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 15 mins-Night: 15 mins | Planned - RESUBMIT | Planned - RESUBMIT |  |  | T | T |  | QLD Maintenance 5 Hours | #REF! | 5 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Kiamal SF - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Horsham - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-04 06:00 | 2025-04-04 16:00 | Horsham - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
NSW | Transgrid | 2025-04-05 05:00 | 2025-04-05 17:00 | Buronga - Red Cliffs (X9) 220 kV line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW / VIC Commissioning 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2025-04-05 05:00 | 2025-04-05 17:00 | Buronga-Balranald (X3) 220kV line | During this planned outage power transfer will be restricted • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW/VIC/SA Commissioning 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2025-04-06 06:00 | 2025-04-06 18:00 | Buronga-Balranald (X3) 220kV line | During this planned outage power transfer will be restricted • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW/VIC/SA Commissioning 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2025-04-06 06:00 | 2025-04-06 18:00 | Buronga - Red Cliffs (X9) 220 kV line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW / VIC Commissioning 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-06 07:00 | 2025-04-08 18:00 | South Morang - Sydenham No.1 500 kV Line | <<This outage has been WITHDRAWN!>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 60 hrs-Night: NA | Withdrawn | Withdrawn | [5 empty] | VIC Maintenance 2.5 Days | #REF! | 2.5 Days
NSW | Transgrid | 2025-04-07 06:00 | 2025-04-07 18:00 | Buronga-Balranald (X3) 220kV line | During this planned outage power transfer will be restricted • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW/VIC/SA Commissioning 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2025-04-07 06:00 | 2025-04-07 18:00 | Buronga - Red Cliffs (X9) 220 kV line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW / VIC Commissioning 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-08 06:00 | 2025-04-08 18:00 | Hazelwood - South Morang No.1 500 kV Line | <<NEW since the last notification>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
TAS | TasNetworks | 2025-04-08 12:00 | 2025-04-08 14:00 | Gordon - Chapel St No.1 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT |  |  |  | T |  | TAS Maintenance 2 Hours | #REF! | 2 Hours
VIC | AusNet | 2025-04-09 06:00 | 2025-04-09 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-10 06:00 | 2025-04-10 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2025-04-10 06:00 | 2025-04-23 18:00 | Buronga - Red Cliffs (X1) 220 kV line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | NSW / VIC Commissioning 13.5 Days | #REF! | 13.5 Days
VIC | AusNet | 2025-04-10 07:00 | 2025-04-15 18:00 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.5 Days | #REF! | 5.5 Days
TAS | TasNetworks | 2025-04-10 08:00 | 2025-04-10 16:00 | Sheffield - Farrell No.2 220 kV Line | A credible contingency event during this planned outage could cause a large reduction in generation in Tasmania. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | TAS Commissioning 8 Hours | #REF! | 8 Hours
VIC | AusNet | 2025-04-11 06:00 | 2025-04-11 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-12 06:00 | 2025-04-12 18:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-15 05:00 | 2025-04-15 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-15 06:00 | 2025-04-15 16:00 | Kiamal SF - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 24 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-16 05:00 | 2025-04-16 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-17 05:00 | 2025-04-17 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-04-17 06:00 | 2025-04-17 16:00 | Bulgana - Horsham 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-17 06:00 | 2025-04-17 16:00 | Crowland - Bulgana 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-17 06:00 | 2025-04-17 16:00 | Kiamal SF - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-21 07:00 | 2025-04-21 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-28 06:00 | 2025-04-28 16:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-04-28 07:00 | 2025-04-30 18:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 24 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 2.5 Days | #REF! | 2.5 Days
VIC | TOA | 2025-04-28 07:00 | 2025-04-28 12:00 | Ararat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: NA-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 5 Hours | #REF! | 5 Hours
VIC | AusNet | 2025-04-29 05:00 | 2025-04-29 17:00 | Haunted Gully - Tarrone 500 Kv line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  | T | T | VIC / SA Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-02 06:00 | 2025-05-02 12:00 | Cressy - Mortlake No.2 500kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 2 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | T |  |  |  |  | VIC / SA Maintenance 6 Hours | #REF! | 6 Hours
VIC | AusNet | 2025-05-02 07:00 | 2025-05-07 18:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.5 Days | #REF! | 5.5 Days
VIC | AusNet | 2025-05-05 07:00 | 2025-05-05 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-05-06 08:00 | 2025-05-09 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 3.4 Days | #REF! | 3.4 Days
VIC | AusNet | 2025-05-07 05:00 | 2025-05-07 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-07 06:00 | 2025-05-07 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-07 07:00 | 2025-05-07 17:00 | Dederang - Wodonga 330 kV Line | This line outage offloads X5 220 kV line. Possible load shedding and risk of large reduction in generation in NSW and interconnector capacity between NSW - Victoria following a credible contingency | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-08 05:00 | 2025-05-08 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-08 06:00 | 2025-05-08 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-08 07:00 | 2025-05-08 17:00 | Dederang - Wodonga 330 kV Line | This line outage offloads X5 220 kV line. Possible load shedding and risk of large reduction in generation in NSW and interconnector capacity between NSW - Victoria following a credible contingency | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-09 05:00 | 2025-05-09 17:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-09 06:00 | 2025-05-09 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 6 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
QLD | Powerlink | 2025-05-12 07:00 | 2025-05-16 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
QLD | Powerlink | 2025-05-12 07:00 | 2025-05-16 17:00 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 6 hrs-Night: 8 hrs | Planned - RESUBMIT | Planned - RESUBMIT |  |  | T |  |  | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-05-12 07:00 | 2025-05-12 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-13 06:00 | 2025-05-13 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 7 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-13 07:00 | 2025-05-13 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-14 06:00 | 2025-05-14 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 7 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-15 06:00 | 2025-05-15 18:00 | Keilor – Sydenham 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 7 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2025-05-19 07:00 | 2025-05-19 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-20 07:00 | 2025-05-20 17:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-05-20 07:00 | 2025-05-27 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 7.4 Days | #REF! | 7.4 Days
VIC | AusNet | 2025-05-21 06:00 | 2025-05-21 19:30 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 13.5 Hours | #REF! | 13.5 Hours
VIC | AusNet | 2025-05-21 07:00 | 2025-05-21 17:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-21 07:00 | 2025-05-21 17:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-22 06:00 | 2025-05-22 19:30 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 13.5 Hours | #REF! | 13.5 Hours
VIC | AusNet | 2025-05-22 07:00 | 2025-05-22 15:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 8 Hours | #REF! | 8 Hours
VIC | AusNet | 2025-05-23 06:00 | 2025-05-23 19:30 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 13.5 Hours | #REF! | 13.5 Hours
VIC | AusNet | 2025-05-24 06:00 | 2025-05-24 19:30 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 3 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 13.5 Hours | #REF! | 13.5 Hours
VIC | AusNet | 2025-05-26 06:00 | 2025-05-26 16:00 | Bulgana - Horsham 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-05-26 07:00 | 2025-05-26 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-05-30 12:00 | 2025-05-30 14:00 | Strathmore - Ross (8857) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 18 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 2 Hours | #REF! | 2 Hours
NSW | Transgrid | 2025-05-31 07:00 | 2025-06-06 18:15 | Wagga - Darlington Point (63) 330 kV Line | This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer •Between Victoria and New South Wales. •Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 18 hrs-Night: 18 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  | T | T | T | NSW/ VIC Commissioning 6.5 Days | #REF! | 6.5 Days
QLD | Powerlink | 2025-06-02 08:00 | 2025-06-06 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
NSW | Transgrid | 2025-06-07 07:00 | 2025-06-08 18:00 | Lower Tumut - Wagga (051) 330 kV Line | This outage offloads the Buronga to Darlington Point X5 220 kV line and restricts power transfer • Between Victoria and New South Wales. • Between South Australia and Victoria on Murraylink A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: 2 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/ VIC Commissioning 1.5 Days | #REF! | 1.5 Days
QLD | Powerlink | 2025-06-07 08:00 | 2025-06-07 11:30 | Haughton River - Ross (8911) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT |  |  |  | T |  | QLD Maintenance 3.5 Hours | #REF! | 3.5 Hours
QLD | Powerlink | 2025-06-09 08:00 | 2025-06-13 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-06-10 07:00 | 2025-06-10 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-10 07:00 | 2025-06-10 17:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-10 07:00 | 2025-06-10 17:00 | Red Cliffs-Wemen 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-11 07:00 | 2025-06-11 17:00 | Horsham - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-11 07:00 | 2025-06-11 17:00 | Red Cliffs-Wemen 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-06-16 08:00 | 2025-06-20 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-06-17 07:00 | 2025-06-17 17:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-17 07:00 | 2025-06-17 17:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | TOA | 2025-06-19 07:00 | 2025-06-19 12:00 | Ararat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 1.5 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 5 Hours | #REF! | 5 Hours
VIC | AusNet | 2025-06-20 07:00 | 2025-06-20 17:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-21 07:00 | 2025-06-21 17:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-22 07:00 | 2025-06-22 17:00 | Red Cliffs - Buronga No.1 (X1) 220kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-06-23 07:00 | 2025-06-23 17:00 | Red Cliffs - Buronga No.1 (X1) 220kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-06-23 07:00 | 2025-06-27 17:00 | Bouldercombe - Broadsound (820) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 5 hrs-Night: 3 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-06-24 07:00 | 2025-06-29 17:00 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #REF! | 5.4 Days
SA | ElectraNet | 2025-06-30 07:30 | 2025-07-06 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
VIC | AusNet | 2025-07-02 07:00 | 2025-07-02 17:00 | Kiamal SF - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-07-02 07:00 | 2025-07-02 17:00 | Bendigo - Kerang 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
SA | ElectraNet | 2025-07-07 07:30 | 2025-07-13 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
VIC | AusNet | 2025-07-11 07:00 | 2025-07-11 17:00 | Cressy - Mortlake No.2 500kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC / SA Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-07-12 07:00 | 2025-07-12 17:00 | Cressy - Mortlake No.2 500kV line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 30 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC / SA Maintenance 10 Hours | #REF! | 10 Hours
SA | ElectraNet | 2025-07-14 07:30 | 2025-07-20 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
VIC | AusNet | 2025-07-15 07:00 | 2025-07-20 17:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #REF! | 5.4 Days
SA | ElectraNet | 2025-07-21 07:30 | 2025-07-27 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2025-07-28 07:30 | 2025-08-03 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2025-08-04 07:30 | 2025-08-10 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
VIC | AusNet | 2025-08-06 06:00 | 2025-08-06 19:30 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | T |  |  |  |  | VIC Maintenance 13.5 Hours | #REF! | 13.5 Hours
VIC | AusNet | 2025-08-08 07:00 | 2025-08-13 17:00 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #REF! | 5.4 Days
QLD | Powerlink | 2025-08-19 08:00 | 2025-11-24 07:59 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 0 mins-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 97 Days | #REF! | 97 Days
VIC | AusNet | 2025-09-01 07:00 | 2025-09-06 17:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 120 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 5.4 Days | #REF! | 5.4 Days
NSW | Transgrid | 2025-09-02 07:00 | 2025-09-13 17:00 | Dumaresq-Sapphire (8J) 330kV LINE | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/QLD Commissioning 11.4 Days | #REF! | 11.4 Days
VIC | AusNet | 2025-09-03 05:30 | 2025-09-03 15:00 | Hazelwood - Loy Yang Power Station No.1 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 0 mins-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 9.5 Hours | #REF! | 9.5 Hours
NSW | Transgrid | 2025-09-15 07:00 | 2025-09-20 17:00 | Dumaresq-Sapphire (8J) 330kV LINE | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW/QLD Commissioning 5.4 Days | #REF! | 5.4 Days
NSW | Transgrid | 2025-09-30 07:00 | 2025-10-11 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 11.4 Days | #REF! | 11.4 Days
VIC | AusNet | 2025-10-02 07:00 | 2025-10-02 17:00 | Crowland - Bulgana 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-02 07:00 | 2025-10-02 17:00 | Crowland - Bulgana 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-06 06:00 | 2025-10-06 16:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-06 07:00 | 2025-10-06 17:00 | South Morang - Sydenham No.1 500 kV Line | <<NEW since the last notification>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 24 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-07 07:00 | 2025-10-07 17:00 | South Morang - Sydenham No.1 500 kV Line | <<NEW since the last notification>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 24 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-08 07:00 | 2025-10-08 17:00 | South Morang - Sydenham No.1 500 kV Line | <<NEW since the last notification>> This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 24 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
NSW | Transgrid | 2025-10-13 06:00 | 2025-10-18 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 5.4 Days | #REF! | 5.4 Days
QLD | Powerlink | 2025-10-13 07:00 | 2025-10-16 12:00 | Strathmore - Ross (8857) 275 kV Line | <<This outage has been WITHDRAWN!>> This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 4 hrs-Night: 6 hrs | Withdrawn | Withdrawn |  |  | T |  |  | Commissioning 3.2 Days | #REF! | 3.2 Days
VIC | AusNet | 2025-10-20 06:00 | 2025-10-20 16:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-10-21 06:00 | 2025-10-21 16:00 | Ballarat - Waubra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-10-21 08:00 | 2025-10-21 16:00 | Nebo - Strathmore (8845) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 2 hrs-Night: 2 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 8 Hours | #REF! | 8 Hours
NSW | Transgrid | 2025-10-28 06:00 | 2025-11-08 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 11.4 Days | #REF! | 11.4 Days
VIC | AusNet | 2025-11-02 06:00 | 2025-11-02 16:00 | Crowland - Bulgana 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
VIC | AusNet | 2025-11-02 06:00 | 2025-11-02 16:00 | Crowland - Bulgana 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
QLD | Powerlink | 2025-11-04 08:00 | 2025-11-07 10:00 | Strathmore - Ross (8857) 275 kV Line | <<NEW since the last notification>> This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 24 hrs-Night: 18 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Commissioning 3.1 Days | #REF! | 3.1 Days
VIC | AusNet | 2025-11-06 06:00 | 2025-11-06 16:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 60 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 10 Hours | #REF! | 10 Hours
NSW | Transgrid | 2025-11-10 06:00 | 2025-11-15 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 5.4 Days | #REF! | 5.4 Days
VIC | AusNet | 2025-11-21 06:00 | 2025-11-21 17:00 | Moorabool–Sydenham No.2 500 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 24 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 11 Hours | #REF! | 11 Hours
VIC | AusNet | 2025-11-22 06:00 | 2025-11-22 17:00 | Moorabool–Sydenham No.2 500 kV Line | <<NEW since the last notification>> A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 24 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 11 Hours | #REF! | 11 Hours
QLD | Powerlink | 2025-11-24 08:00 | 2025-11-28 17:00 | Nebo - Strathmore (822) 275 kV Line | This is a high impact outage because the recall time is greater than 30 minutes. A credible contingency event during this planned outage may require market intervention through issuing of directions. | Day: 48 hrs-Night: 48 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | QLD Maintenance 4.4 Days | #REF! | 4.4 Days
VIC | AusNet | 2025-12-11 06:00 | 2025-12-11 15:30 | South Morang - Sydenham No.2 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9.5 Hours | #REF! | 9.5 Hours
VIC | AusNet | 2025-12-12 06:00 | 2025-12-12 15:30 | South Morang - Sydenham No.1 500 kV Line | This is a high impact outage only if the Forecast Operational Demand in Victoria region is greater than 7,000 MW A credible contingency event during this planned outage could: • Cause a large reduction in generation in Victoria • Restrict power transfer across the Victoria - South Australia interconnector (Heywood interconnector). | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 9.5 Hours | #REF! | 9.5 Hours
VIC | AusNet | 2025-12-17 06:00 | 2025-12-17 14:00 | Kiamal SF-Red Cliffs 220 kV LINE | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 8 Hours | #REF! | 8 Hours
VIC | AusNet | 2025-12-31 06:00 | 2025-12-31 17:00 | Kiamal SF - MurraWarra 220 kV Line | A credible contingency event during this planned outage may require: • Load shedding in the Victorian outer grid • Market intervention through issuing of directions. | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 11 Hours | #REF! | 11 Hours
VIC | AusNet | 2025-12-31 06:30 | 2025-12-31 15:00 | Hazelwood - Loy Yang Power Station No.1 500 kV Line | A credible contingency event during this planned outage could cause: • A large reduction in generation in Victoria • Load shedding in Victoria | Day: 1 hr-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 8.5 Hours | #REF! | 8.5 Hours
VIC | AusNet | 2026-01-21 06:00 | 2026-01-21 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-01-22 06:00 | 2026-01-22 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-11 06:00 | 2026-02-11 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 2 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-20 06:00 | 2026-02-20 18:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-21 06:00 | 2026-02-21 18:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-22 06:00 | 2026-02-22 18:00 | Moorabool–Sydenham No.2 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-23 06:00 | 2026-02-23 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
VIC | AusNet | 2026-02-25 06:00 | 2026-02-25 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2026-03-17 06:00 | 2026-03-28 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 11.4 Days | #REF! | 11.4 Days
VIC | AusNet | 2026-03-24 06:00 | 2026-03-24 18:00 | Moorabool–Sydenham No.1 500 kV Line | A credible contingency event during this planned outage may require market intervention through issuing of directions | Day: 4 hrs-Night: NA | Planned - RESUBMIT | Planned - RESUBMIT | [5 empty] | VIC Maintenance 12 Hours | #REF! | 12 Hours
NSW | Transgrid | 2026-03-30 06:00 | 2026-04-04 16:00 | Armidale - Dumaresq (8C) 330 kV Line | A credible contingency event during this planned outage could cause: • Synchronous separation of the Queensland region from the rest of the NEM | Day: 12 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | NSW / QLD Commissioning 5.4 Days | #REF! | 5.4 Days
SA | ElectraNet | 2026-06-29 07:30 | 2026-07-05 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2026-07-06 07:30 | 2026-07-12 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2026-07-13 07:30 | 2026-07-19 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
SA | ElectraNet | 2026-07-20 07:30 | 2026-07-26 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2026-07-27 07:30 | 2026-08-02 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2026-08-03 07:30 | 2026-08-09 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2027-06-28 07:30 | 2027-07-04 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2027-07-05 07:30 | 2027-07-11 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2027-07-12 07:30 | 2027-07-18 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
SA | ElectraNet | 2027-07-19 07:30 | 2027-07-25 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2027-07-26 07:30 | 2027-08-01 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2027-08-02 07:30 | 2027-08-08 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2028-06-26 07:30 | 2028-07-02 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2028-07-03 07:30 | 2028-07-09 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2028-07-10 07:30 | 2028-07-16 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
SA | ElectraNet | 2028-07-17 07:30 | 2028-07-23 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2028-07-24 07:30 | 2028-07-30 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2028-07-31 07:30 | 2028-08-06 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2029-07-02 07:30 | 2029-07-08 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2029-07-09 07:30 | 2029-07-15 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2029-07-16 07:30 | 2029-07-22 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
SA | ElectraNet | 2029-07-23 07:30 | 2029-07-29 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2029-07-30 07:30 | 2029-08-05 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2029-08-06 07:30 | 2029-08-12 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2030-07-01 07:30 | 2030-07-07 17:30 | Tailem Bend - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2030-07-08 07:30 | 2030-07-14 17:30 | Tailem Bend - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2030-07-15 07:30 | 2030-07-21 19:30 | Heywood - South East No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.5 Days | #REF! | 6.5 Days
SA | ElectraNet | 2030-07-22 07:30 | 2030-07-28 17:30 | Heywood - South East No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT |  |  |  |  | T | VIC / SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2030-07-29 07:30 | 2030-08-04 17:30 | Tailem Bend - Tungkillo No.1 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
SA | ElectraNet | 2030-08-05 07:30 | 2030-08-11 17:30 | Tailem Bend - Tungkillo No.2 275 kV Line | A credible contingency event during this planned outage could cause synchronous separation of the South Australia region from the rest of the NEM. During this planned outage: • Power transfer will be restricted across the Victoria - South Australia interconnector (Heywood interconnector). • Post contingent FCAS will be sourced within SA following Separation event. | Day: 6 hrs-Night: 12 hrs | Planned - SUBMIT | Planned - SUBMIT | [5 empty] | SA Maintenance 6.4 Days | #REF! | 6.4 Days
Withdrawn / UTP since the last notification